PANEL TEST REPORT

PANEL DETAILS

| Parameter | Value |
| --- | --- |
| Substation | REF-3 SS-1 |
| Switchboard | HV-201A |
| Panel No. | P-01 |
| Test Date | 2026-08-17 |
| Feed Equipment | 201-MG-01A |
| Equipment Type | Motor |
| Number of CTs | 3 |
| Numerical Relays | 1 |
| Auxiliary Relays | 2 |

INSTALLED TEST COMPONENTS

| Component | Type | Manufacturer | Model | Serial Number |
| --- | --- | --- | --- | --- |
| CT-01 | CT | Jyoti |  |  |
| CT-02 | CT |  |  |  |
| CT-03 | CT |  |  |  |
| REL-01 | NUMERICAL_RELAY |  |  |  |
| AUX-01 | AUXILIARY_RELAY |  |  |  |
| AUX-02 | AUXILIARY_RELAY |  |  |  |
| M-01 | METER | RISH |  |  |
| M-02 | METER |  |  |  |

TEST SUMMARY

| Test ID | Date | Test Type | Component | Result |
| --- | --- | --- | --- | --- |
| TEST-3508DA01 | 2026-08-17 | METER | M-02 | PARTIALLY TESTED |

COMPONENT TEST DETAILS

M-02 - METER

| Parameter | Value |
| --- | --- |
| Meter Type | Multifunction Meter |

METER MEASUREMENT RESULTS

| Function | Applied Value | Recorded Value | Tolerance % | Error % | Result |
| --- | --- | --- | --- | --- | --- |
| VOLTAGE | 1.0 | 1.0 | 0.5 | 0.0 | PASS |
| CURRENT | 13.0 | 13.0 | 0.5 | 0.0 | PASS |
| FREQUENCY | 50.0 | 50.0 | 0.5 | 0.0 | PASS |
| ACTIVE_POWER | 120.0 | 120.0 | 0.5 | 0.0 | PASS |
| REACTIVE_POWER | 0.0 | 0.0 | 0.5 |  | NOT TESTED |
| APPARENT_POWER | 0.0 | 0.0 | 0.5 |  | NOT TESTED |
| POWER_FACTOR | 0.0 | 0.0 | 0.5 |  | NOT TESTED |

Result: PARTIALLY TESTED

OVERALL PANEL RESULT

Result: PARTIALLY TESTED

TESTING / APPROVAL

| Tested By |  |
| --- | --- |
| Reviewed By |  |
| Date / Signature |  |