AUXILIARY RELAY TEST REPORT

RELAY IDENTIFICATION

| Parameter | Value |
| --- | --- |
| Test ID | TEST-5A94477F |
| Test Date | 2026-08-15T17:05:02 |
| Component ID | CMP-29878E03 |
| Manufacturer | XYZZZ |
| Model |  |
| Serial Number | 123455 |
| Coil Voltage | 110 |
| Contact Configuration | 2 NO 3 NC |

COIL PICKUP / DROPOUT TEST

| Parameter | Value |
| --- | --- |
| Rated Coil Voltage | 110 |
| Pickup Voltage | 73 |
| Pickup Voltage (%) | 66.36 |
| Dropout Voltage | 25 |
| Dropout Voltage (%) | 22.73 |

OPERATING TIME

| Parameter | Value |
| --- | --- |
| Expected Pickup Time | 200 |
| Measured Pickup Time | 190 |
| Pickup Time Error (%) | -5.00 |
| Expected Dropout Time | 200 |
| Measured Dropout Time | 201 |
| Dropout Time Error (%) | 0.50 |

CONTACT OPERATION

| Parameter | Value |
| --- | --- |
| Expected Operation | OPERATE |
| Observed Operation | OPERATE |
| Functional Result | PASS |

TEST RESULT

PASS

REMARKS