PANEL TEST REPORT

PANEL DETAILS

| Parameter | Value |
| --- | --- |
| Substation | REF-3 SS-1 |
| Switchboard | HV-201A |
| Panel No. | P-01 |
| Test Date | 2026-08-15 |
| Feed Equipment | 201-MG-01A |
| Equipment Type | Motor |
| Number of CTs | 3 |
| Numerical Relays | 1 |
| Auxiliary Relays | 2 |
| Meters | 2 |

INSTALLED TEST COMPONENTS

| Component | Type | Manufacturer | Model | Serial Number |
| --- | --- | --- | --- | --- |
| CT-01 | CT | Jyoti |  |  |
| CT-02 | CT |  |  |  |
| CT-03 | CT |  |  |  |
| REL-01 | NUMERICAL_RELAY |  |  |  |
| AUX-01 | AUXILIARY_RELAY |  |  |  |
| AUX-02 | AUXILIARY_RELAY |  |  |  |
| M-01 | METER | RISH |  |  |
| M-02 | METER |  |  |  |

TEST SUMMARY

| Test ID | Date | Test Type | Component | Result |
| --- | --- | --- | --- | --- |
| TEST-8D3DD7CC | 2026-08-15 | METER | M-01 | PASS |
| TEST-5A94477F | 2026-08-15 | AUX_RELAY | AUX-01 | PASS |
| TEST-500300F6 | 2026-08-15 | CT | CT-01 | PASS |
| TEST-7F4B2008 | 2026-08-15 | CT | CT-01 | PASS |
| TEST-9AA59253 | 2026-08-15 | CT | CT-01 | PASS |
| TEST-F2B94B69 | 2026-08-15 | 51N | REL-01 | PASS |
| TEST-741A1C83 | 2026-08-15 | 51N | REL-01 | PASS |
| TEST-D89ACA73 | 2026-08-15 | 51N | REL-01 | PASS |
| TEST-E09EB605 | 2026-08-15 | 50N | REL-01 | PASS |
| TEST-CB31DFA5 | 2026-08-15 | 51 | REL-01 | PASS |
| TEST-601CB33E | 2026-08-15 | 50 | REL-01 | PASS |
| TEST-D93AAB3F | 2026-08-15 | 50N | REL-01 | PASS |
| TEST-58C64958 | 2026-08-15 | 51 | REL-01 | PASS |
| TEST-84888904 | 2026-08-15 | 50 | REL-01 | PASS |

COMPONENT TEST DETAILS

M-01 - METER

| Parameter | Value |
| --- | --- |
| Meter Type | Ammeter |
| Accuracy Class | 10 |

METER MEASUREMENT RESULTS

| Function | Applied Value | Recorded Value | Tolerance % | Error % | Result |
| --- | --- | --- | --- | --- | --- |
| CURRENT | 10.0 | 10.0 | 10.0 | 0.0 | PASS |

Result: PASS

AUX-01 - AUX_RELAY

| Parameter | Value |
| --- | --- |
| Manufacturer | XYZZZ |
| Serial Number | 123455 |
| Coil Voltage | 110 |
| Contact Configuration | 2 NO 3 NC |
| Rated Voltage | 110 |
| Pickup Voltage | 73 |
| Pickup Voltage Percent | 66.36 |
| Dropout Voltage | 25 |
| Dropout Voltage Percent | 22.73 |
| Expected Pickup Time | 200 |
| Pickup Time | 190 |
| Pickup Time Error | -5.00 |
| Expected Dropout Time | 200 |
| Dropout Time | 201 |
| Dropout Time Error | 0.50 |
| No Contact Result | PASS |
| Nc Contact Result | PASS |
| Expected Operation | OPERATE |
| Observed Operation | OPERATE |
| Functional Result | PASS |
| Tolerance Percent | 5 |
| Result | PASS |

Result: PASS

CT-01 - CT

| Parameter | Value |
| --- | --- |
| Ct Primary | 0.0 |
| Ct Secondary | 0.0 |
| Nominal Current | 0.0 |
| Ct Ratio | 200/1 |
| Core | Protection |
| Ct Class | 5P20 |
| Burden | 10 |
| Manufacturer | Jyoti |
| Primary Current | 100 |
| Secondary Current | 0.503 |
| Measured Ratio | 198.8072 |
| Expected Polarity | REVERSE |
| Observed Polarity | REVERSE |
| Polarity Result | PASS |
| Tolerance Percent | 5 |
| Result | PASS |

Result: PASS

CT-01 - CT

| Parameter | Value |
| --- | --- |
| Ct Ratio | 200 |
| Core | Protection |
| Ct Class | 5P20 |
| Burden | 10 |
| Manufacturer | Jyoti |
| Primary Current | 201 |
| Secondary Current | 1 |
| Measured Ratio | 201.0000 |
| Expected Polarity | CORRECT |
| Observed Polarity | CORRECT |
| Tolerance Percent | 5 |
| Result | PASS |

Result: PASS

CT-01 - CT

| Parameter | Value |
| --- | --- |
| Ct Ratio | 200 |
| Core | Protection |
| Ct Class | 5P20 |
| Burden | 10 |
| Primary Current | 100 |
| Secondary Current | 0.5 |
| Measured Ratio | 200.0000 |
| Expected Polarity | REVERSE |
| Observed Polarity | REVERSE |
| Polarity Result | PASS |
| Burden Test Current | 10 |
| Measured Burden | 10 |
| Tolerance Percent | 5 |
| Result | PASS |

Result: PASS

PROTECTION TEST DETAILS

REL-01 - 51N

| Parameter | Value |
| --- | --- |
| Pickup Current | 0.01 |
| Test Current | 0.6 |
| Curve | IEC-NI |
| Tms | 0.1 |
| Psm | 60.000 |
| Pickup Current A | 0.0100 |
| Test Current A | 0.6000 |
| Expected Time | 0.1641 |
| Actual Time | 0.17 |
| Error Percent | 3.60 |
| Tolerance Percent | 5.0 |
| Result | PASS |
| Nominal Current A | 1.0 |
| Nominal Current Unit | A |
| Ct Id | CMP-625D41FB |
| Ct Name | CT-01 |
| Ct Primary A | 30.0 |
| Ct Secondary A | 1.0 |
| Ct Ratio | 30/1 |

Result: PASS

REL-01 - 51N

| Parameter | Value |
| --- | --- |
| Pickup Current | 0.01 |
| Test Current | 0.6 |
| Curve | IEC-NI |
| Tms | 0.15 |
| Psm | 60.000 |
| Pickup Current A | 0.0100 |
| Test Current A | 0.6000 |
| Expected Time | 0.2461 |
| Actual Time | 0.25 |
| Error Percent | 1.58 |
| Tolerance Percent | 5.0 |
| Result | PASS |
| Nominal Current A | 1.0 |
| Nominal Current Unit | A |
| Ct Id | CMP-625D41FB |
| Ct Name | CT-01 |
| Ct Primary A | 30.0 |
| Ct Secondary A | 1.0 |
| Ct Ratio | 30/1 |

Result: PASS

REL-01 - 51N

| Parameter | Value |
| --- | --- |
| Pickup Current | 0.01 |
| Test Current | 0.6 |
| Curve | IEC-NI |
| Tms | 0.1 |
| Psm | 50.000 |
| Pickup Current A | 0.0100 |
| Test Current A | 0.5000 |
| Expected Time | 0.1720 |
| Actual Time | 0.173 |
| Error Percent | 0.58 |
| Tolerance Percent | 5.0 |
| Result | PASS |

Result: PASS

REL-01 - 50N

| Parameter | Value |
| --- | --- |
| Pickup Current | 0.1 |
| Test Current | 0.101 |
| Pickup Current A | 0.1000 |
| Test Current A | 0.1010 |
| Pickup Error Percent | 1.00 |
| Tolerance Percent | 5.0 |
| Result | PASS |
| Nominal Current A | 1.0 |
| Nominal Current Unit | A |
| Ct Id | CMP-625D41FB |
| Ct Name | CT-01 |
| Ct Primary A | 30.0 |
| Ct Secondary A | 1.0 |
| Ct Ratio | 30/1 |

Result: PASS

REL-01 - 51

| Parameter | Value |
| --- | --- |
| Pickup Current | 0.4 |
| Test Current | 1 |
| Curve | IEC-NI |
| Tms | 0.4 |
| Psm | 2.500 |
| Pickup Current A | 0.4000 |
| Test Current A | 1.0000 |
| Expected Time | 3.0279 |
| Actual Time | 3.1 |
| Error Percent | 2.38 |
| Tolerance Percent | 5.0 |
| Result | PASS |
| Nominal Current A | 1.0 |
| Nominal Current Unit | A |
| Ct Id | CMP-625D41FB |
| Ct Name | CT-01 |
| Ct Primary A | 30.0 |
| Ct Secondary A | 1.0 |
| Ct Ratio | 30/1 |

Result: PASS

REL-01 - 50

| Parameter | Value |
| --- | --- |
| Pickup Current | 0.2 |
| Test Current | 0.201 |
| Pickup Current A | 0.2000 |
| Test Current A | 0.2010 |
| Pickup Error Percent | 0.50 |
| Tolerance Percent | 5.0 |
| Result | PASS |
| Nominal Current A | 1.0 |
| Nominal Current Unit | A |
| Ct Id | CMP-625D41FB |
| Ct Name | CT-01 |
| Ct Primary A | 30.0 |
| Ct Secondary A | 1.0 |
| Ct Ratio | 30/1 |

Result: PASS

REL-01 - 50N

| Parameter | Value |
| --- | --- |
| Pickup Current | 100 |
| Test Current | 101 |
| Pickup Error Percent | 1.00 |
| Tolerance Percent | 5.0 |
| Result | PASS |

Result: PASS

REL-01 - 51

| Parameter | Value |
| --- | --- |
| Pickup Current | 10 |
| Test Current | 100 |
| Curve | IEC-NI |
| Tms | 0.2 |
| Psm | 10.000 |
| Expected Time | 0.5941 |
| Actual Time | 0.6 |
| Error Percent | 0.99 |
| Tolerance Percent | 5.0 |
| Remarks | passes |
| Result | PASS |

Result: PASS

Remarks: passes

REL-01 - 50

| Parameter | Value |
| --- | --- |
| Pickup Current | 100 |
| Test Current | 101 |
| Pickup Error Percent | 1.00 |
| Tolerance Percent | 5.0 |
| Remarks | Passed |
| Result | PASS |

Result: PASS

Remarks: Passed

OVERALL PANEL RESULT

Result: PASS

TESTING / APPROVAL

| Tested By |  |
| --- | --- |
| Reviewed By |  |
| Date / Signature |  |