PANEL TEST REPORT

PANEL DETAILS

| Parameter | Value |
| --- | --- |
| Substation | REF-3 SS-1 |
| Switchboard | HV-201A |
| Panel No. | P-01 |
| Test Date | 2026-08-17 |
| Feed Equipment | 201-MG-01A |
| Equipment Type | Motor |
| Number of CTs | 3 |
| Numerical Relays | 1 |
| Auxiliary Relays | 2 |
| Meters | 2 |

INSTALLED TEST COMPONENTS

| Component | Type | Manufacturer | Model | Serial Number |
| --- | --- | --- | --- | --- |
| CT-01 | CT | Jyoti |  |  |
| CT-02 | CT |  |  |  |
| CT-03 | CT |  |  |  |
| REL-01 | NUMERICAL_RELAY |  |  |  |
| AUX-01 | AUXILIARY_RELAY |  |  |  |
| AUX-02 | AUXILIARY_RELAY |  |  |  |
| M-01 | METER | RISH |  |  |
| M-02 | METER |  |  |  |

TEST SUMMARY

| Test ID | Date | Test Type | Component | Result |
| --- | --- | --- | --- | --- |
| TEST-C219855C | 2026-08-17 | CT | CT-02 | PASS |
| TEST-295AE630 | 2026-08-17 | METER | M-01 | PASS |
| TEST-952A6DF2 | 2026-08-17 | CT | CT-01 | PASS |
| TEST-79C0792D | 2026-08-17 | 51 | REL-01 | PASS |

COMPONENT TEST DETAILS

CT-02 - CT

| Parameter | Value |
| --- | --- |
| Ct Primary | 30.0 |
| Ct Secondary | 1.0 |
| Nominal Current | 1 |
| Ct Ratio | 30/1 |
| Core | Metering |
| Ct Class | Class 1 |
| Burden | 10 |
| Expected Polarity | CORRECT |
| Observed Polarity | CORRECT |
| Polarity Result | PASS |
| Tolerance Percent | 5 |
| Result | PASS |
| Is Three Phase | True |
| Ct Name | CT-02 |

PHASE-WISE CT TEST RESULTS

| Phase | Measured Ratio | Ratio Error % | Result | Test No | Primary Current | Secondary Current |
| --- | --- | --- | --- | --- | --- | --- |
| R | 30.3030 | 1.01 | PASS | 1 | 30 | 0.99 |
| R | 30.3030 | 1.01 | PASS | 2 | 10 | 0.33 |
| Y | 29.9850 | -0.05 | PASS | 1 | 20 | 0.667 |
| B | 29.9401 | -0.20 | PASS | 1 | 30 | 1.002 |
| B | 30.0000 | 0.00 | PASS | 2 | 15 | 0.5 |
| B | 31.2500 | 4.17 | PASS | 3 | 10 | 0.32 |

Result: PASS

M-01 - METER

| Parameter | Value |
| --- | --- |
| Meter Type | Multifunction Meter |
| Accuracy Class | 10 |

METER MEASUREMENT RESULTS

| Function | Applied Value | Recorded Value | Tolerance % | Error % | Result |
| --- | --- | --- | --- | --- | --- |
| VOLTAGE | 110.0 | 110.0 | 10.0 | 0.0 | PASS |
| CURRENT | 1.0 | 1.02 | 10.0 | 2.0000000000000018 | PASS |

Result: PASS

CT-01 - CT

| Parameter | Value |
| --- | --- |
| Ct Primary | 30.0 |
| Ct Secondary | 1.0 |
| Nominal Current | 1 |
| Ct Ratio | 30/1 |
| Core | Protection |
| Ct Class | 5P20 |
| Burden | 10 |
| Manufacturer | Jyoti |
| Expected Polarity | CORRECT |
| Observed Polarity | CORRECT |
| Polarity Result | PASS |
| Ir Primary Earth | 100 |
| Ir Secondary Earth | 20 |
| Ir Test Voltage | 2500 |
| Ir Test Duration | 60 |
| Resistance Phase A | 1.2 |
| Resistance Phase B | 1.2 |
| Resistance Phase C | 1.2 |
| Burden Test Current | 10 |
| Measured Burden | 10.1 |
| Burden Error | 1.00 |
| Tolerance Percent | 5 |
| Result | PASS |
| Is Three Phase | True |
| Ct Name | CT-01 |

PHASE-WISE CT TEST RESULTS

| Phase | Measured Ratio | Ratio Error % | Primary Current | Secondary Current |
| --- | --- | --- | --- | --- |
| R | 30.0000 | 0.00 | 30 | 1 |
| Y | 30.3030 | 1.01 | 30 | 0.99 |
| B | 29.7030 | -0.99 | 30 | 1.01 |

Result: PASS

PROTECTION TEST DETAILS

REL-01 - 51

| Parameter | Value |
| --- | --- |
| Pickup Current | 0.5 |
| Test Current | 1.2 |
| Curve | IEC-NI |
| Tms | 0.4 |
| Psm | 2.400 |
| Pickup Current A | 0.5000 |
| Test Current A | 1.2000 |
| Expected Time | 3.1704 |
| Actual Time | 3.45 |
| Error Percent | 8.82 |
| Tolerance Percent | 10 |
| Result | PASS |
| Nominal Current A | 1.0 |
| Nominal Current Unit | A |
| Ct Id | CMP-625D41FB |
| Ct Name | CT-01 |
| Ct Primary A | 30.0 |
| Ct Secondary A | 1.0 |
| Ct Ratio | 30/1 |

Result: PASS

OVERALL PANEL RESULT

Result: PASS

TESTING / APPROVAL

| Tested By |  |
| --- | --- |
| Reviewed By |  |
| Date / Signature |  |